{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["Sheet1"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":145,"n_cols":7,"rows_kept":145,"merged":[[0,0,0,6],[13,1,13,3],[14,1,14,6],[40,1,40,3],[41,1,41,6],[59,0,61,0],[59,1,61,1],[59,2,61,2],[63,0,65,0],[63,1,65,1],[63,2,65,2],[91,1,91,3],[92,1,92,6],[101,1,101,6],[109,1,109,6],[127,1,127,6],[134,2,134,6],[135,1,135,6]],"flags":["formulas_cached_only"]}
["客户名称: 深圳市大族数控科技股份有限公司        工程量:联昇厂房一楼         "]
["序号",null,"单位","数量","单价","合计","材料结构及制造安装工艺"]
["一","拆除工程"]
[1,"砖墙拆除","m²",{"v":17.5,"d":"17.50"},null,null,"砖墙拆除人工费"]
[2,"拆除石膏板天花","m²",{"v":95,"d":"95.00"},null,null,"吊顶使用的材料需全部拆除，墙孔恢复"]
[3,"拆除彩钢板天花","m²",{"v":333,"d":"333.00"},null,null,"吊顶使用的材料需全部拆除，墙孔恢复"]
[4,"拆除彩钢板墙","m²",{"v":101,"d":"101.00"},null,null,"人工（墙孔不需要恢复，原位置做砖墙）"]
[5,"管道拆除","米",{"v":3,"d":"3.00"},null,null,"墙面修复，人工"]
[6,"门洞扩大","m²",{"v":2.2,"d":"2.20"},null,null,"现有尺寸3*2.8，要求尺寸3*3.5，拆除后安装电动卷闸门"]
[7,"电动卷闸门","项",{"v":1,"d":"1.00"},null,null,"要求使用尺寸3*3.5米"]
[8,"拆墙痕迹修补","项",{"v":1,"d":"1.00"},null,null,"砖墙痕迹和吊顶痕迹"]
[9,"脚手架（升高车）","项",1,null,null,"活动脚手架或者高空车费用"]
[10,"垃圾外运清理","车",1,null,null,"垃圾清理费用"]
[null,"小计"]
["二","      增加工程"]
[1,"新做砖墙","m²",{"v":101,"d":"101.00"},null,null,"砖墙200厚，要求在宽4.5米的位置增加构造柱，在高3米的位置增加横梁，门框要求增加构造柱，材料费，砌墙，粉刷，批白人工费。"]
[2,"补砖墙","m²",{"v":22,"d":"22.00"},null,null,"修补化学品仓、洗手间墙面及新建空压机房隔墙。门框要求增加横梁，材料费，砌墙，粉刷，批白人工费。"]
[4,"砖墙门洞","m²",{"v":4.8,"d":"4.80"},null,null,"要求高2.4米，宽2米，双开防火门，门框增加构造柱（车间门）"]
[5,"开砖墙门洞","m²",{"v":2,"d":"2.00"},null,null,"要求高2米，宽1米，（空压机门）"]
[6,"双开防火门","m²",{"v":4.8,"d":"4.80"},null,null,"甲级防火门，高2.4米，宽2米"]
[7,"单开防火门","m²",5.28,null,null,"甲级防火门，宽1.2*2.2，（化学品仓和空压机房各1扇）"]
[8,"封门洞","m²",{"v":2,"d":"2.00"},null,null,"车间现有防火门封堵，要求砖墙封堵，0.9*2.2，材料、人工"]
[9,"砖墙刷白","m²",{"v":244,"d":"244.00"},null,null,"人工、辅料（车间隔墙）（化学品仓、空压机房、洗手间）"]
[10,"新建办公室砖墙","m²",{"v":75,"d":"75.00"},null,null,"砖墙180厚、要求在长4.5米的位置增加构造柱，在高3米的位置增加横梁，门框要求增加构造柱，宽3*6.2、长9*6.2、材料  人工"]
[11,"办公室双开防火门","m²",{"v":3,"d":"3.00"},null,null,"甲级双开防火门门1.5米*2.1米.辅料，人工"]
[12,"吊石膏板天花","m²",{"v":27,"d":"27.00"},null,null,"规格600*600  材料，人工（办公室）"]
[13,"天花龙骨","m²",{"v":27,"d":"27.00"},null,null,"主付龙骨，8厘吊杆，"]
[14,"新建卫生间","项",{"v":1,"d":"1.00"},null,null,"要求隔断使用防水耐火的抗倍特板材，厚度12mm，宽度1.2米，深度1.4米，高度1.9米，材料，人工，3位"]
[15,"卫生间地漏","项",{"v":1,"d":"1.00"},null,null,"50排水管，挖槽埋地60宽，深150"]
[16,"新建卫生间吊顶","m²",{"v":15.5,"d":"15.50"},null,null,"铝扣板吊顶、规格300*300、材料，人工"]
[17,"吊顶龙骨","m²",{"v":15.5,"d":"15.50"},null,null,"主付龙骨，8厘吊杆，"]
[18,"洗手间照明","盏",{"v":5,"d":"5.00"},null,null,"300*300，16瓦，雷士，欧普"]
[19,"新建水池（洗清洁用品）","项",{"v":1,"d":"1.00"},null,null,"要求建在卫生间内，尺寸：600*600*600，贴瓷砖"]
[20,"开凿地面","米",{"v":48,"d":"48.00"},null,null,"卫生间污水管接入污水池，埋160mmPVC管，人工"]
[21,"化学品房间地面防水","m²",{"v":10,"d":"10.00"},null,null,"要求铺砖，做防水，刷油漆。"]
[22,"化学品房间排水地漏","米",{"v":22,"d":"22.00"},null,null,"联塑，PVC50排水管。"]
[23,"开墙孔","个",{"v":1,"d":"1.00"},null,null,"开圆孔650MM   人工（排气管用）"]
[24,"脚手架（升高车）","项",1,null,null,"活动脚手架或者高空车费用"]
[25,"材料搬运费","项",1,null,null,"人工搬运"]
[26,"垃圾清运","车",1,null,null,"垃圾外运"]
[null,"小计"]
["三","  照明，电气系统项目"]
[1,"300*150*1.5线槽","米",{"v":180,"d":"180.00"},null,null,"300*150*1.5镀锌铁线槽，连接片，螺丝"]
[2,"线槽支架","米",{"v":180,"d":"180.00"},null,null,"40万能角铁。"]
[3,"配电箱（1）","个",{"v":1,"d":"1.00"},null,null,"要求含电流表、电压表、指示灯。配置800A总制1个  630A开关1个   100A空开1个（办公室空调、插座使用）200A空开1个（正泰，32A工业插使用）"]
[4,"配电箱（2）","个",{"v":1,"d":"1.00"},null,null,"要求含电流表  电压表  指示灯配置800A总制1个  630A开关1个  \n  200A空开1个（正泰，32A工业插使用），100A空开1个（风机使用）"]
[5,"配电箱（3）","个",{"v":1,"d":"1.00"},null,null,"配置630A开关1个，从配电箱1的800A开关出线"]
[6,"配电箱（4）","个",{"v":1,"d":"1.00"},null,null,"配置630A开关1个，从配电箱2的800A开关出线"]
[7,"配电箱（5）","个",{"v":1,"d":"1.00"},null,null,"要求含电流表、电压表、指示灯。配置630A总制1个 正泰"]
[8,"电箱","个",{"v":18,"d":"18.00"},null,null,"1、电箱内安装一个3P32A漏电开关、一个2P16A漏电开关、人工（按距离和功率在电箱1和电箱2分出"]
[9,"漏电开关","个",{"v":18,"d":"18.00"},null,null,"3P32A漏电、辅料、人工"]
[10,"漏电开关","个",{"v":17,"d":"17.00"},null,null,"2P16A220V、辅料、人工"]
[11,"32A防水插座","个",{"v":18,"d":"18.00"},null,null,"威浦三相五芯32A防水插座，3P32A漏电开关接出"]
[12,"32A防水插头"," 个",{"v":18,"d":"18.00"},null,null,"威浦三相五芯32A防水插头"]
[13,"32防水插电线","米",{"v":3400,"d":"3400.00"},null,null,"成天泰BVV4m²电线（材料）5*4平方"]
[14,"防水插座安装接线","个",{"v":18,"d":"18.00"},null,null,"4m²，人工"]
[15,"绝缘板","块",{"v":17,"d":"17.00"},null,null,"350*200绝缘板，爆炸螺丝固定"]
[16,"电源插座","个",{"v":17,"d":"17.00"},null,null,"松本，曼科220V、10A、8孔插座,2P漏电开关接出"]
[17,"插座电线","项",{"v":17,"d":"17.00"},null,null,"成天泰BVV2.5m²电线，"]
[18,"单芯电缆线","米",{"v":480,"d":"480.00"},null,null,"成天泰单芯3*185（2组）（门口600A电箱)相线"]
[{"$nulls":3},{"v":160,"d":"160.00"},null,null,"成天泰单芯150电缆（2组）零线"]
[{"$nulls":3},{"v":160,"d":"160.00"},null,null,"成天泰单芯120电缆（2组）地线"]
[19,"拉电缆人工","米",{"v":800,"d":"800.00"},null,null,"拉电缆人工。"]
[20,"单芯电缆线","米",{"v":918,"d":"918.00"},null,null,"成天泰单芯3*300电缆（2组）(600A2个开关、630A开关1个)相线"]
[{"$nulls":3},{"v":306,"d":"306.00"},null,null,"成天泰单芯240电缆（2组）零线"]
[{"$nulls":3},{"v":306,"d":"306.00"},null,null,"成天泰单芯185电缆（2组）地线"]
[21,"拉电缆人工","米",{"v":1530,"d":"1530.00"},null,null,"拉电缆人工。"]
[22,"漏电开关","个",10,null,null,"2P25A漏电开关，正泰（办公用）"]
[23,"空气开关","个",5,null,null,"3P32A空开5个，正泰（办公用）"]
[24,"电箱","个",{"v":5,"d":"5.00"},null,null,"12位胶电箱，致业（办公用）"]
[25,"办公室电源插座","个",{"v":40,"d":"40.00"},null,null,"松本，曼科220V、10A、8孔插座,2P漏电开关接出"]
[26,"办公室插座灯电线","米",{"v":300,"d":"300.00"},null,null,"成天泰BVV2.5m²电线，"]
[27,"线管","米",120,null,null,"联塑PVC线管，32线管"]
[28,"车间LED防爆灯","个",{"v":65,"d":"65.00"},null,null,"LED100W防爆灯，佛山照明，三雄激光。"]
[29,"防爆灯电源电线","米",{"v":2400,"d":"2400.00"},null,null,"成天泰BVV2.5m²电线，"]
[30,"防爆灯线管","米",{"v":280,"d":"280.00"},null,null,"镀锌线管6分"]
[31,"防爆灯安装","个",{"v":65,"d":"65.00"},null,null,"材料，人工"]
[32,"防爆灯开关","个",{"v":24,"d":"24.00"},null,null,"1P10A空气开关，正泰（照明开关）"]
[33,"电箱","个",{"v":3,"d":"3.00"},null,null,"3个12位胶电箱，致业（照明开关用）"]
[34,"拆除防爆灯","盏",12,null,null,"办公室防爆灯拆除人工"]
[35,"拆除防爆灯","盏",36,null,null,"车间灯拆除人工"]
[36,"拆除防爆灯线路","米",90,null,null,"线路拆除人工"]
[37,"电箱","个",1,null,null,"12位胶电箱，致业（化学品仓库用）"]
[38,"国标电线","米",150,null,null,"成天泰BVV6m²电线，（空压机、化学品仓，洗手间）"]
[39,"排气扇","个",3,null,null,"正野天花排气扇，管道，人工辅料。（洗手间）"]
[40,"防爆风扇","个",1,null,null,"220V，0.5KW，1450R/MIN（电线要求钢管布线，开关放在外面）管道，人工辅料"]
[41,"防爆灯","套",2,null,null,"开关安装在房间的外面，里面钢管布线（双灯管防爆灯）(化学仓库、空压机房各1个）使用，线管，人工，辅料"]
[42,"摇头壁扇","台",20,null,null,"安装在32A电源的柱子上，电压220V，规格650MM，转速1400rpm，人工，辅料"]
[43,"天花平板LED灯","个",24,null,null,"规格600*600 ，36瓦，雷士，欧普材料，人工（办公室）"]
[44,"材料搬运费","项",1,null,null,"人工搬运"]
[45,"垃圾清运","车",{"$nulls":3},"垃圾外运"]
[null,"       小计"]
["四","       弱电项目"]
[1,"网线","m",600,null,null,"山泽 6类网线、PVC线管、配件"]
[2,"网络面板","个",25,null,null,"安普6类，网络需求25位"]
[3,"PVC线管","m",200,null,null,"PVC线槽   联塑，25管"]
[4,"网络交换机","个",1,null,null,"华为 S5735-L48T4S-A非POE交换机48口  "]
[5,"网络机柜","个",1,null,null,"图腾机柜， 24U"]
[6,"配线架","m",1,null,null,"华为6类"]
[7,"材料搬运费","项",1,null,null,"人工搬运"]
[null,"小计"]
["五","       监控项目"]
[1,"枪式网络摄像机","台",13,null,null,"海康威视  200万像素摄像头"]
[2,"摄像机主机","台",1,null,null,"海康、16口"]
[3,"硬盘","个",2,null,null,"西数或者希捷硬盘，存储60天"]
[4,"支架","套",13,null,null,"国产，海康"]
[5,"交换机","台",1,null,null,"普联,24口交换机"]
[6,"网线","m",900,null,null,"山泽6类网线、PVC线管、配件"]
[null,"小计"]
["六","    车间气管，水管"]
[1,"气管","米",{"v":100,"d":"100.00"},null,null,"32mmPPR管联塑"]
[2,"气管配件","个",{"v":50,"d":"50.00"},null,null,"32mmPPR管联塑配件，弯头，三通，直通"]
[3,"气管吊码及人工","米",{"v":100,"d":"100.00"},null,null,"10厘螺杆，角铁，人工辅料"]
[4,"快插接头","个",{"v":7,"d":"7.00"},null,null,"不锈钢接头"]
[5,"球阀","个",{"v":17,"d":"17.00"},null,null,"联塑球阀，人工安装"]
[6,"辅料","项",{"v":1,"d":"1.00"},null,null,"各种辅料"]
[7,"PPR水管","米",{"v":100,"d":"100.00"},null,null,"要求主管安装50mm，联塑   "]
[8,"PPR水管","米",{"v":50,"d":"50.00"},null,null,"要求支管安装25mm，联塑"]
[9,"水龙头","个",{"v":7,"d":"7.00"},null,null,"胶龙头"]
[10,"球阀","个",{"v":17,"d":"17.00"},null,null,"联塑25mm球阀，人工安装"]
[11,"球阀","个",{"v":4,"d":"4.00"},null,null,"联塑50mm球阀，人工安装"]
[12,"水管吊码及人工","米",{"v":100,"d":"100.00"},null,null,"10厘螺杆，角铁，人工辅料"]
[13,"洗眼器","个",{"v":2,"d":"2.00"},null,null,"304不锈钢材质、安装材料，人工"]
[14,"排水管","米",70,null,null,"联塑50排水管，长度确认（洗眼器排水管）"]
[15,"脚手架或者高空车","项",{"v":1,"d":"1.00"},null,null,"设备费用"]
[16,"材料运输费","项",{"v":1,"d":"1.00"},null,null,"货车运输费"]
[null,"小计"]
["七","       车间抽风"]
[1,"抽风管道","米","46（外面）+85（车间）",null,null,"650mm管径   阻燃PP材料，联塑（东西18米的位置留三通，南北18米的位置留三通，三通口和南北两端的管口用法兰堵住"]
[2,"抽风管道配件","个",{"v":30,"d":"30.00"},null,null,"650mm弯头，三通，直通   联塑"]
[3,"气管吊码及人工","米",{"v":110,"d":"110.00"},null,null,"角铁，人工辅料"]
[4,"防腐通风机","台",1,null,null,"酸性气体，要求风叶玻璃纤维材质、风流量最少达到10000立方/小时，风机暂定15KW"]
[5,"风机电源线，10平方","米","280+200",null,null,"主线为10平方电线3*10+2*6（加上办公室区域总电源电线）"]
[6,"风机控制电箱","个",1,null,null,"配置控制开关，要求能控制风机启停"]
[null,"小计"]
["八","       消防工程"]
[1,"消防疏散指示牌","套",20,null,null,"劳士（左右各10个）"]
[2,"安全出口指示灯","个",15,null,null,"劳士"]
[3,"应急灯","个",30,null,null,"劳士（危化品仓要求安装防爆应急灯以及指示牌）"]
[4,"1.5平方电线","m",800,null,null,"成天泰，金环宇"]
[5,"镀锌线管","m",200,null,null,"20镀锌管"]
[null,"小计"]
[{"$nulls":3},"合计"]
[{"$nulls":3},"税金"]
[{"$nulls":3},"总计"]